## DTSU666_DTSU666H
Chint description |  |  | CHINT order | CHINT HEX | CHINT DEC | HUAW DEC | Huawei HEX | HUAWEI order | Huawei description | liczba bajtów | dzielnik | typ zmiennej
Line line voltage (uab) | V | float | 0 | 2000 | 8192 | 2118 | 846 | 8 | A-B line voltage | 2 |  | float | V
Line line voltage (ubc) | V | float | 1 | 2002 | 8194 | 2120 | 848 | 9 | B-C line voltage | 2 |  | float | V
Line line voltage (uca) | V | float | 2 | 2004 | 8196 | 2122 | 84A | 10 | C-A line voltage | 2 |  | float | V
Phase phase voltage (ua) | V | float | 3 | 2006 | 8198 | 2110 | 83E | 4 | Phase A Voltage | 2 |  | float | V
Phase phase voltage (ub) | V | float | 4 | 2008 | 8200 | 2112 | 840 | 5 | Phase B Voltage | 2 |  | float | V
Phase phase voltage (uc) | V | float | 5 | 200A | 8202 | 2114 | 842 | 6 | Phase C Voltage | 2 |  | float | V
The data of three phase current (ia) | A | float | 6 | 200C | 8204 | 2102 | 836 | 0 | Phase A current | 2 |  | float | A
The data of three phase current (ib) | A | float | 7 | 200E | 8206 | 2104 | 838 | 1 | Phase B current | 2 |  | float | A
The data of three phase current (ic) | A | float | 8 | 2010 | 8208 | 2106 | 83A | 2 | Phase C current | 2 |  | float | A
Conjunction active power (pt) | W | float | 9 | 2012 | 8210 | 2126 | 84E | 12 | Active Power | 2 | 1000 | float | kW
A phase active power (pa) | W | float | 10 | 2014 | 8212 | 2128 | 850 | 13 | Phase A Active Power | 2 | 1000 | float | kW
B phase active power (pb) | W | float | 11 | 2016 | 8214 | 2130 | 852 | 14 | Phase B Active Power | 2 | 1000 | float | kW
C phase active power (pc) | W | float | 12 | 2018 | 8216 | 2132 | 854 | 15 | Phase C Active Power | 2 | 1000 | float | kW
Conjunction reactive power (qt) | var | float | 13 | 201A | 8218 | 2134 | 856 | 16 | Reactive Power | 2 | 1000 | float | kVar
A phase reactive power (qa) | var | float | 14 | 201C | 8220 | 2136 | 858 | 17 | A phase reactive power (qa) |  |  | float | kVar
B phase reactive power (qb) | var | float | 15 | 201E | 8222 | 2138 | 85A | 18 | B phase reactive power (qb) |  |  | float | kVar
C phase reactive power (qc) | var | float | 16 | 2020 | 8224 | 2140 | 85D | 19 | C phase reactive power (qc) |  |  | float | kVar
|  |  | 17 | 2022 | 8226 | 2142 | 85E | 20 | Apparent Power – total | 2 | 1000 | float | kVA
|  |  | 18 | 2024 | 8228 | 2144 | 860 | 21 | Phase A – Apparent Power |  |  | float | kVA
|  |  | 19 | 2026 | 8230 | 2146 | 862 | 22 | Phase B – Apparent Power |  |  | float | kVA
|  |  | 20 | 2028 | 8232 | 2148 | 864 | 23 | Phase C – Apparent Power |  |  | float | kVA
Conjunction power factor (pft) cos fi |  | float | 21 | 202A | 8234 | 2150 | 866 | 24 | Power Factor |  |  | float
A phase power factor (invalid when three phase three wire) (pfa) |  | float | 22 | 202C | 8236 | 2152 | 868 | 25 | Power Factor A | 2 |  | float
B phase power factor (invalid when three phase three wire) (pfb) |  | float | 23 | 202E | 8238 | 2154 | 86A | 26 | Power Factor B | 2 |  | float
C phase power factor (invalid when three phase three wire) (pfc) |  | float | 24 | 2030 | 8240 | 2156 | 86D | 27 | Power Factor C | 2
???? |  |  | 25 | 2032 | 8242 |  |  |  |  | 2 |  | float
???? |  |  | 26 | 2034 | 8244 | 2160 | 870 | 29 | ????
???? |  |  | 27 | 2036 | 8246 | 2162 | 872 | 30 | ????
???? |  |  | 28 | 2038 | 8248 | 2164 | 874 | 31 | ????
???? |  |  | 29 | 203A | 8250 |  | 876 | 44 | ????
???? |  |  | 30 | 203C | 8252 | 2168 | 878 | 33 | ????
???? |  |  | 31 | 203E | 8254 | 2170 | 87A | 34 | ????
???? |  |  | 32 | 2040 | 8256 | 2172 | 87D | 35 | ????
???? |  |  | 33 | 2042 | 8258 |  | 87E | 45 | ????
Frequency (freq) |  |  | 34 | 2044 | 8260 | 2124 | 84C | 11 | Frequency |  |  |  | Hz
???? |  | float | 35 | 2046 | 8262 | 2178 | 882 | 38 | ???? |  |  | float
???? |  |  | 36 | 2048 | 8264 | 2180 | 884 | 39 | ????
???? |  |  | 37 | 204A | 8266 | 2182 | 886 |  | ???? | 2
???? |  |  | 38 | 204C | 8268 | 2184 | 88A |  | ????
???? |  |  | 39 | 204E | 8270 | 2186 | 88C |  | ????
Total active power demand (dmpt) |  | float | 40 | 2050 | 8272 | 2158 | 86E | 28 | Total active electricity |  | 1000 | float | kWh
Positive active total (current, import) |  |  | 41 | 401E | 16414 | 2166 | 876 | 32 | Total positiv Active electricity | 2 |  | float | kWh
Negative active total energy (current,export) |  |  | 46 | 4028 | 16424 | 2174 | 87E | 36 | Total negative Active electricity | 2 |  | float | kWh
[6 empty] | 2108 | 83C | 3 | ????
[6 empty] | 2116 | 844 | 7 | ????
[6 empty] | 2176 | 880 | 37 | ????
UPPER REGISTERS |  |  | 41 | 401E | 16414
|  |  | 42 |  | 16416
|  |  | 43 |  | 16418
|  |  | 44 |  | 16420
|  |  | 45 |  | 16422
|  |  | 46 | 4028 | 16424
|  |  | 47 |  | 16426
|  |  | 49 |  | 16428
|  |  | 50 |  | 16430
|  |  | 51 |  | 16432
Quadrant 1 reactive total energy (current) |  | float | 52 | 4032 | 16434 | [6 empty] | float
|  |  | 53 |  | 16436
|  |  | 54 |  | 16438
|  |  | 55 |  | 16440
|  |  | 56 |  | 16442
Quadrant 2 reactive total energy (current) |  | float | 57 | 403C | 16444 | [6 empty] | float
|  |  | 58 |  | 16446
|  |  | 59 |  | 16448
|  |  | 60 |  | 16450
|  |  | 61 |  | 16452
Quadrant 3 reactive total energy (current) |  | float | 62 | 4046 | 16454 | [6 empty] | float
|  |  | 63 |  | 16456
|  |  | 64 |  | 16458
|  |  | 65 |  | 16460
|  |  | 66 |  | 16462
Quadrant 4 reactive total energy (current) |  | float | 67 | 4050 | 16464 | [6 empty] | float
Programming password code |  | smallint |  |  | 1
Electric energy zero clearing clr.e |  | smallint |  |  | 2
Current transformer ratio (irat) |  | smallint |  |  | 6
Potentia1 transformer ratio (urat) |  | smallint |  |  | 7
Meter type (meter type) |  | smallint |  |  | 11
Second |  | smallint |  |  | 47
Minute |  | smallint |  |  | 48
Hour |  | smallint |  |  | 49
Day |  | smallint |  |  | 50
Month |  | smallint |  |  | 51
Year |  | smallint |  |  | 52
czynna |  |  | 644
bierna |  |  | 271
pozorna |  |  | 698.6966
cosfi |  |  | 0.92172